BACKFLOW  PREVENTION  ASSEMBLY  TEST  REPORT

| NEW INSTALLATION | ANNUAL TEST | REPLACEMENT | REPAIRS |
| --- | --- | --- | --- |

FACILITY NAME:  ASSISI CENTRE

FACILITY ADDRESS:  230 ROSANNA ROAD, ROSANNA, VIC  3084

Customer Name:  PLUMBCO PLUMBERS

Customer Address:  P.O. Box 299, PORT MELBOURNE, VIC  3207

Water Authority:  YARRA VALLEY WATER

DEVICE DETAILS

| CONTAINMENT | ZONE |  INDIVIDUAL | - Meter No: |
| --- | --- | --- | --- |

| SERIAL No: 73682 | MAKE: Tyco | MODEL: RP 03 |
| --- | --- | --- |
| DEVICE SIZE: 20 mm | DEVICE TYPE: RPZD | TAG No: |

DEVICE LOCATION:  ZONE FOR DIRTY UTILITY ROOM IN STAINLESS BOX (COLD) ON FIRST FLOOR STAGE 2.

INSTALLED TO AUSTRALIAN STANDARDS A.S.3500:	 YES 	 NO

| # TEST RESULTS | Reduced Pressure Zone Device |  |  |  |
| --- | --- | --- | --- | --- |
|  | # Double Check Valve Assembly |  |  | RELIEF VALVE |
|  | # DCV/RPZ # CHECK VALVE NO.1 | # DCV/RPZ # CHECK VALVE NO.2 |  |  |
| # INITIAL TEST  PASSED  FAILED |  CLOSED TIGHT 26 KPA  LEAKED |  CLOSED TIGHT KPA  LEAKED |  | OPENED AT KPA #1 CHECK KPA  AIR GAP OK? |
| Test After Repairs  PASSED  FAILED |  CLOSED TIGHT 50 KPA |  CLOSED TIGHT 17 KPA |  | OPENED AT 21 KPA #1 CHECK KPA |

1ST CHECK FAILED INITIAL TEST - CLEANED DEBRIS OUT OF CHECK VALVE (TEFLON) - CLEANED STRAINER - RE-TEST PASSED.

TESTING REMARKS:

INSTALL REMARKS:

TESTED BY: Andrew Meade	LICENCE. NO. 33250	SIGNED:  ____________________________

Test Kit Serial No: AC-14193	Test Kit Calibration Date: 19/02/2014 	Test Date: 16/09/2013

TEST PASSED: YES      NO           WATER SERVICE RESTORED: YES      NO  	NEXT TEST DUE: 14-Dec-13