ASSISI REDEVELOPMENT PROJECT DESCRIPTION OF SUPPLIED EQUIPMENT

Short description of the functionality and operation:

The following sections detail a short description of the equipment supplied by COMTEL technologies and the basic operation of each system. Further details can be sought from the detailed product manuals also supplied in the separate sections of this manual.

Nursecall System: - The system installed is a Questek manufactured product and is designed to inform staff when a patient / resident, requires help in the form of staff assistance. Each Residential Care room contains a bed point comprising of a call, assist, Out of bed and wet bed indications. Each Ensuite has a call/assist point in the room with a separate shower slave callpoint. There is an additional button on the toilet rail not supplied by COMTEL but is connected to the nursecall to give a call indication in the required room. All this ensures patients can activate calls from either shower or toilet or room. The assist button in each designated room is utilised by staff when they require additional staff to help. Common rooms also have callpoints where residents may be left unattended and if required they can call for help by staff.

When the nursecall buttons are pressed a message is sent to dedicated SpectraLink WiFi VOIP telephones in text message formats alerting staff a resident requires help. The message is also displayed on displays throughout the facilities nurse bases. Depending on the call type the display and built in sounder will alert differently. A ding is for standard calls, two short dings repetitively are for assist calls and continuous dings are for duress and emergency calls if installed on the system.

SpectraLink:- The WiFi VOIP system is a Polycom product comprising of 25 handsets connected via WiFi Access points positioned around the facility to allow staff to roam within the building whilst being able to make and receive phones calls. In addition each handset can receive messages from the nursecall and security systems. Specific handsets will receive messages from certain nursecall points that have been previously configured.

Access Control System:- The access control system consists of keypads and electric locks. Each electronically locked door will allow access to persons who know a valid code for entry to the main doors via the keypads. If a keypad is at the door then a valid code entered will grant access. When a fire alarm is presented at the FIP it will send a signal to the security which will in turn unlock dedicated doors allowing all persons to exit doors normally locked. Specifically nominated doors that do not have access control are monitored and if required will send an alarms to nominated equipment when a door is opened outside of normal operating conditions.

Door Phone:-

Dallas Delta door phones are utilised at main entry doors to the facility. When the single button is pressed it calls a dedicated group 777 in the PABX and pre programmed numbers are in this group. The phones receive the call and when answered by the staff member they can, by pressing a specific sequence on the phone keypad, grant access to the caller into the building.

CCTV System:- The Closed Circiut Television System comprises of multiple cameras. The DVR’s are networked through the IP system allowing configuration from any PC on the network that knows the correct user name and password. The DVR can be set to motion recording or constant and can even set the area you wish to have for motion activation.

Patient Wanderer System:- The patient wanderer system comprises of multiple receivers placed at dedicated doors to trigger into alarm when a programmed tag worn by a resident comes within a pre defined range. Once alarmed, the signal is sent to the nursecall via a closed contact and in turn is then transmitted to the displays and cordless handsets in the form of a message. Each tag is programmed to each receiver unit .

Data Network :- The data network consists of a series of cables running from the end point back to a distribution rack where the data cable connects to a network switch provided by ASSISI’s IT contractor.

Each cable is terminated on a patch panel to make connectivity and cable point identification easier.

Interfacing between all systems:- There are many systems operating at the facililty and some interface to the nursecall in some way. Following is a brief description of the interface types. Some systems interface via what is called high level and some interface via low level:

- High Level Interfacing – This is when the sending or receiving equipment sends a packet of data from an output port on said equipment. The nursecall system then receives this packet of data and if it is the correct format and layout required it then acts on this via some software programming and raises an alarm in the nursecall system.

- Low Level Interfacing – This is the basic form of alarms and is when a relay output is supplied in the form of either a normally open or closed contact.

Following is a list of the interface types and how they connect:

- Security – High level interface sending pre defined alarms

- Fire Indication Panel – High Level interface sending pre defined alarms and low level to the Security panel

- Patient Wanderer – Low level interface to the nursecall.

- Spectralink – High level to the nursecall receiving nursecall alarms