

PROJECT REPORT

Project name and address: Assisi Aged care 230 Rosanna Road Rosanna

Date of site attendance: 26-6-2014

M.E Technician: A Parsons

Reason for site visit: Set controls AG150 and E.C’s stage.

Setup controls

Note: E.C 1 has units on schematic E.C 2 and E.C 2 has units on Schematic E.C 1

M-nets 26 and 27 have been removed. Informed that units have been replaced with M-series split units.

D.I.D.O and the PEFFY (Fresh Air unit) are on separate networks. Have set up interlocking pin. Program set and ordered I.C pin will return to site to enter. Program set to turn on Fresh air unit in Auto mode 22° This will operate when input to D.I.D.O form 3rd Party CO2 control.

E.C software updated to V 1.95 and AG150 software V 2.95

Additional units added to Comms Room M-nets 20,21

1 x unit requires replacement P.C.B. This has been ordered.